## Table 1 - Eastern Bypass Point
Point Name | Description | Point Type | Station Name | Station Highest Alarm Priority | Status | Analog Value | Limit State | Security Zone | Training Mode Point | Device Class | ADR CommLine | ADR RTU No. | ADR Point No. | ADR Object Type | ADR ClassCode | FormatCode | Annunciation Delay | PrefixSuffixCode | Suffix 0 | Suffix 1 | Suffix 2 | Suffix 3 | Prefix 0 | Prefix 1 | AlarmFormatCode | State 0 Alarm Severity | State 1 Alarm Severity | State 2 Alarm Severity | State 3 Alarm Severity | State 0 VoiceCode | State 1 VoiceCode | State 2 VoiceCode | State 3 VoiceCode | Close Control ADR CommLine | Close Control ADR RTU No. | Close Control ADR Point No. | Close Control Object Type | Close Control Variation Type | Close Control Code + Mode | Open Control ADR CommLine | Open Control ADR RTU No. | Open Control ADR Point No. | Open Control Object Type | Open Control Variation | Open Control Code + Mode | Control Interval | Device Response Timeout | Units | Scaling Factor | Scale Offset | Zero Clamp Deadband | L1 HI alarm | L1 LO alarm | L1 Deadband | L1 HI Alarm Severity | L1 LO Alarm Severity | L1 HI Alarm VoiceCode | L1 LO Alarm VoiceCode | L2 HI Alarm Limit | L2 LO Alarm Limit | L2 Deadband | L2 HI Alarm Severity | L2 LO Alarm Severity | L2 HI Alarm VoiceCode | L2 LO Alarm VoiceCode | L3 HI Alarm Limit | L3 LO Alarm Limit | L3 Deadband | L3 HI Alarm Severity | L3 HI Alarm VoiceCode | L3 LO Alarm VoiceCode | Return to Normal Severity | Rate of Change Limit | Rate of Change Alarm Severity | Rate of Change VoiceCode | Jog Amount
EB1 | EASTERN BYPASS SUBSTATIO |  | EB1 | 4 |  | 0 |  | _,2,3,_,_,_,_,_ | - |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,48DC1A | BATTERY CHARGER #1 AMPS | VOLTAGE | EB1 | 0 |  | 4.17 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 67 | 30 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,48DC1V | BATTERY BANK 1 VOLTS | VOLTAGE | EB1 | 0 |  | 52.79 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 65 | 30 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLT | 0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,4B10 | BUS BKR #1 BYPASS SWITCH | GOABS | EB1 | 0 | OPEN | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4B1L | BUS BKR#1 LOAD SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4B1S | BUS BKR#1 SOURCE SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F1L | FEEDER #1 LOAD SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F1S | FEEDER #1 SOURCE SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F1T | FEEDER #1 TRANSFER SWTCH | GOABS | EB1 | 0 | OPEN | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F2L | FEEDER #2 LOAD SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F2S | FEEDER #2 SOURCE SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F2T | FEEDER #2 TRANSFER SWTCH | GOABS | EB1 | 0 | OPEN | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F3L | FEEDER #3 LOAD SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F3S | FEEDER #3 SOURCE SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F3T | FEEDER #3 TRANSFER SWTCH | GOABS | EB1 | 0 | OPEN | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F4L | FEEDER #4 LOAD SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F4S | FEEDER #4 SOURCE SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F4T | FEEDER #4 TRANSFER SWTCH | GOABS | EB1 | 0 | OPEN | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F5L | FEEDER #5 LOAD SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F5S | FEEDER #5 SOURCE SWITCH | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4F5T | FEEDER #5 TRANSFER SWTCH | GOABS | EB1 | 0 | OPEN | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4M13 | MAIN TIE BETWEEN #1 & #3 | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4M24 | MAIN TIE BETWEEN #2 & #4 | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4M34 | MAIN TIE BETWEEN #3 & #4 | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,4T12 | TRANSF SWITCH BETWEEN 1& | GOABS | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,86TCM1 | TRIP COIL FAIL LOR #1 | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 220 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1-AMX | BUS 1A MAX CURRENT | CURRENT | EB1 | 0 |  | 596.405 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,B1-BMX | BUS 1B MAX CURRENT | CURRENT | EB1 | 0 |  | 606.854 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,B1-CMX | BUS 1C MAX CURRENT | CURRENT | EB1 | 0 |  | 525.699 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,B169EM | B1 MECHANICAL TRIP | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 88 | 1 | 0 | 1 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1ASTP | EBYP B1 CAPS ACT STEP | LDMCAPS | EB1 | 0 |  | 0 | N | 1,_,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | STEP | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,B1BKR | B1 EBYP BUS BREAKER | BUS BKR | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 80 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 131 | 4 | 0 | 0 | 0 | 2 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1BPD | EBYP B1 BILLING PT | LDMCAPS | EB1 | 0 | AUTO | 0 |  | 1,_,_,_,_,_,_,_ | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 23 | DEACTV | AUTO | MANUAL | EXTRNL |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1CAP | BUS #1 CAP IN SERVICE | KVAR | EB1 | 0 |  | 2850 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,B1CMOD | EBYP BUS #1 CAP MODE | CAPBANK | EB1 | 0 | DEACTV | 0 |  | 1,_,_,_,_,_,_,_ | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 23 | DEACTV | AUTO | MANUAL | EXTRNL |  |  | 24 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1COM | BUS#1 RELAY COMM. FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 68 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1ENB | B1 RELAY SELF CHECK ALM | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 69 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1INS | B1 INST TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 70 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1INSB | B1 INST TRIP BLOCK | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 77 | 1 | 0 | 1 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1LOAC | BUS#1 LOSS OF AC ALARM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 89 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1LODC | BUSBKR #1 LOSS OF DC ALM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 87 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1PF | BUS #1 POWER FACTOR | PFACTOR | EB1 | 0 |  | -0.99807 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,B1PFHI | BUS #1 PF HI LIMIT | PFACTOR | EB1 | 0 |  | 1 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,B1PFLO | BUS #1 PF LOW LIMIT | PFACTOR | EB1 | 0 |  | 0.995 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,B1PUA | B1 SEL RELAY PICK UP ALM | PICKUP | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 76 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 140 | 0 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1RSTP | EBYP B1 REQ STEP | LDMCAPS | EB1 | 0 |  | 0 | N | 1,_,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | STEP | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,B1SLO | B1 SLOW OPERATION ALARM | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 81 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1SPR | B1 SPRING CHARGE ALARM | IED | EB1 | 0 | CHRGED | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 82 | 1 | 0 | 0 | 10 | 28 | CHRGED | DISCHG |  |  | CHRGED | DISCHG | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1STRN | EBYP B1 CAPS STRG NUMBER | LDMCAPS | EB1 | 0 |  | 0 | N | 1,_,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | NUMBER | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,B1TCM1 | B1 TRIP COIL ALM #1 FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 78 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1TCM2 | B1 TRIP COIL ALM #2 FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 79 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1TGA | B1 A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 72 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1TGB | B1 B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 73 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1TGC | B1 C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 74 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1TGN | B1 NEUT TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 75 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,B1TIM | B1 TIME TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 71 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,BATVLT | BATTERY BANK#1 VOLT M871 | VOLTAGE | EB1 | 0 |  | 52.5467 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 678 | 30 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLT | 0.0045776 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,BCHERR | BCH ERROR COUNT | SPARE | EB1 | 0 |  | 1 | N | _,2,3,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,BNKLO1 | EBYP BANK #1 LOCKOUT | LOCKOUT | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 221 | 1 | 0 | 0 | 0 | 12 | RESET | LCKOUT |  |  |  |  | 130 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,C1COM | BATT#1 CHARGER COMM FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 13 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,C1DCHI | BATT#1 CHARGER HIGH DC | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 15 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,C1DCLO | BATT#1 CHARGER LOW DC AL | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 14 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,C1LOAC | BATT#1 CHARGER LOSS AC | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 21 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,C1NGND | BATT#1 CHARGER NEG ALM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 20 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,C1PGND | BATT#1 CHARGER POS ALM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 19 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,C403OF | EBYP GRP 40-3 OPEN LIMIT | KVAR | EB1 | 0 |  | 0 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,C403ON | EBYP GRP 40-3 CLSE LIMIT | KVAR | EB1 | 0 |  | 0 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,CAP25 | 25 MVAC CAPACITOR BANK | CAPBANK | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 214 | 1 | 0 | 0 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 24 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 167 | 12 | 1 | 1 | 16 | 47 | 166 | 12 | 1 | 1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,CAPBAL | EBYP 115 CAP BANK ALARM | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 224 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,CAPLO | 25 MVAC CAP BANK LOCKOUT | FDR LO | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 225 | 1 | 0 | 0 | 0 | 12 | RESET | LCKOUT |  |  |  |  | 144 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,CKTSW1 | EBYP CIRCUIT SWITCHER #1 | CKT SW | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 35 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 131 | 4 | 0 | 0 | 0 | 3 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,CNT1 | NO OF CUSTOMERS ON EB-1 | CUST | EB1 | 0 |  | 675 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,CNT2 | NO OF CUSTOMERS ON EB-2 | CUST | EB1 | 0 |  | 377 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,CNT3 | NO OF CUSTOMERS ON EB-3 | CUST | EB1 | 0 |  | 756 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,CNT4 | NO OF CUSTOMERS ON EB-4 | CUST | EB1 | 0 |  | 688 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,CNT5 | NO OF CUSTOMERS ON EB-5 | CUST | EB1 | 0 |  | 768 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,CNTB1 | NO OF CUSTOMERS ON EB-B1 | CUST | EB1 | 0 |  | 4213 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,EFSCA1 | EBYP ENABLE FAST SCAN | SPARE | EB1 | 0 | NORM | 0 |  | _,_,3,_,_,_,_,_ | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 31 | NORM | FAST |  |  | NORM | FAST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,EFSCAN | EBYP ENABLE FAST SCAN | SPARE | EB1 | 0 | NORM | 0 |  | _,_,3,_,_,_,_,_ | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 31 | NORM | FAST |  |  | NORM | FAST | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,ENTRY1 | EBYP ENTRY FRONT GATE | SECURTY | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 419 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 134 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,ENTRY2 | EBYP ENTRY XFMR SIDE | SECURTY | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 420 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 134 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,ENTRY3 | EBYP ENTRY REAR GATE | SECURTY | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 421 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 134 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,ENTRY4 | EBYP ENTRY HOUSE SIDE | SECURTY | EB1 | 0 | ALARM | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 422 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1-A | CKT #1 A-PHASE CURRENT | CURRENT | EB1 | 0 |  | 51 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 539 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F1-B | CKT #1 B-PHASE CURRENT | CURRENT | EB1 | 0 |  | 57 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 540 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F1-C | CKT #1 C-PHASE CURRENT | CURRENT | EB1 | 0 |  | 95 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 541 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F1-N | CKT #1 NEUTRAL CURRENT | CURRENT | EB1 | 0 |  | 41 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 542 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F169EM | CKT#1 MECHANICAL TRIP | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 244 | 1 | 0 | 1 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1ALT1 | CKT#1 ALT MIN TRIP | IED | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 229 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 34 | 12 | 1 | 1 | 16 | 47 | 34 | 12 | 1 | 1 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1AR | CKT#1 AUTO-RECLOSE | AUTORCL | EB1 | 0 | AUTO | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 231 | 1 | 0 | 0 | 0 | 3 | 1-SHOT | AUTO |  |  | 1-SHOT | AUTO | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 35 | 12 | 1 | 4 | 16 | 47 | 35 | 12 | 1 | 3 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1BKR | CKT#1 EBYP | FDR BKR | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 230 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 140 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 16 | 47 | 146 | 12 | 1 | 41 | 16 | 47 | 147 | 12 | 1 | 21 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1CAP | FEEDER #1 CAP IN SERVICE | KVAR | EB1 | 0 |  | 450 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,F1COM | CKT#1 COMM. FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 228 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1ENB | CKT#1 CONTROL FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 233 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1GT | CKT#1 GROUND TRIP | GNDTRIP | EB1 | 0 | NORMAL | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 232 | 1 | 0 | 0 | 0 | 4 | BYPASS | NORMAL |  |  | BYPASS | NORMAL | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 31 | 12 | 1 | 0 | 16 | 47 | 31 | 12 | 1 | 1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1HLT | CKT#1 HOT LINE TAGGED | AUTORCL | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 250 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 20 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1INS | CKT#1 INST TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 253 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1INSB | CKT#1 INST TRIP BLOCK | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 254 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1KVAR | CKT#1 KVAR DEMAND | KW | EB1 | 0 |  | 125 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 547 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F1KW | CKT#1 KW DEMAND | KW | EB1 | 0 |  | 1438 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 546 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KW | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F1LOAC | CKT#1 LOSS OF AC ALARM | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 243 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1LODC | CKT#1 LOSS DC ALARM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 240 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1LOUT | EBYP FDR LOCKOUT #1 | FDR LO | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 239 | 1 | 0 | 0 | 0 | 12 | RESET | LCKOUT |  |  |  |  | 141 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1LR | CKT#1 LOCAL/REMOTE | IED | EB1 | 0 | REMOTE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 245 | 1 | 0 | 1 | 0 | 21 | LOCAL | REMOTE |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1PF | FEEDER #1 PF CALC | PFACTOR | EB1 | 0 |  | 1 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F1PF-T | CKT#1 PF TELEMETERED | PFACTOR | EB1 | 0 |  | -2.27 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 548 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | -0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F1PUA | CKT#1 RELAY PICKUP ALARM | PICKUP | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 238 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 140 | 0 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1RST | CKT#1 RESET TARGETS | IED | EB1 | 0 | RESET | 0 |  | 1,2,3,4,5,6,7,8 | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | 16 | 47 | 29 | 12 | 1 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1SLO | CKT#1 SLOW OPERATION ALM | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 246 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1SPR | CKT#1 SPRING CHARGE ALRM | IED | EB1 | 0 | CHRGED | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 242 | 1 | 0 | 1 | 10 | 28 | CHRGED | DISCHG |  |  | CHRGED | DISCHG | 140 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1TCM | CKT#1 TRIP COIL FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 237 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1TGA | CKT#1 A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 234 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1TGB | CKT#1 B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 235 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1TGC | CKT#1 C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 236 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1TGN | CKT#1 NEUTRAL TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 251 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F1TIM | CKT#1 TIME TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 252 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2-A | CKT #2 A-PHASE CURRENT | CURRENT | EB1 | 0 |  | 102 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 556 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F2-B | CKT #2 B-PHASE CURRENT | CURRENT | EB1 | 0 |  | 89 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 557 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F2-C | CKT #2 C-PHASE CURRENT | CURRENT | EB1 | 0 |  | 69 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 558 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F2-N | CKT #2 NEUTRAL CURRENT | CURRENT | EB1 | 0 |  | 34 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 559 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F269EM | CKT#2 MECHANICAL TRIP | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 278 | 1 | 0 | 1 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2ALT1 | CKT#2 ALT MIN TRIP | IED | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 256 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 56 | 12 | 1 | 1 | 16 | 47 | 56 | 12 | 1 | 1 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2AR | CKT#2 AUTO-RECLOSE | AUTORCL | EB1 | 0 | AUTO | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 258 | 1 | 0 | 0 | 0 | 3 | 1-SHOT | AUTO |  |  | 1-SHOT | AUTO | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 57 | 12 | 1 | 4 | 16 | 47 | 57 | 12 | 1 | 3 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2BKR | CKT#2 EBYP | FDR BKR | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 257 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 140 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 16 | 47 | 148 | 12 | 1 | 41 | 16 | 47 | 149 | 12 | 1 | 21 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2CAP | FEEDER #2 CAP IN SERVICE | KVAR | EB1 | 0 |  | 1050 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,F2COM | CKT#2 COMM. FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 255 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2ENB | CKT#2 CONTROL FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 260 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2GT | CKT#2 GROUND TRIP | GNDTRIP | EB1 | 0 | NORMAL | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 259 | 1 | 0 | 0 | 0 | 4 | BYPASS | NORMAL |  |  | BYPASS | NORMAL | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 53 | 12 | 1 | 0 | 16 | 47 | 53 | 12 | 1 | 1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2HLT | CKT#2 HOT LINE TAGGED | AUTORCL | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 284 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 20 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2INS | CKT#2 INST TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 287 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2INSB | CKT#2 INST TRIP BLOCK | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 275 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2KVAR | CKT#2 KVAR DEMAND | KW | EB1 | 0 |  | -763 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 564 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F2KW | CKT#2 KW DEMAND | KW | EB1 | 0 |  | 1713 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 563 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KW | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F2LOAC | CKT#2 LOSS OF AC ALARM | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 277 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2LODC | CKT#2 LOSS DC ALARM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 273 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2LOUT | EBYP FDR LOCKOUT #2 | FDR LO | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 272 | 1 | 0 | 0 | 0 | 12 | RESET | LCKOUT |  |  |  |  | 141 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2LR | CKT#2 LOCAL/REMOTE | IED | EB1 | 0 | REMOTE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 279 | 1 | 0 | 1 | 0 | 21 | LOCAL | REMOTE |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2PF | FEEDER #2 PF CALC | PFACTOR | EB1 | 0 |  | -0.91664 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F2PF-T | CKT#2 PF TELEMETERED | PFACTOR | EB1 | 0 |  | -0.92 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 565 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | -0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F2PUA | CKT#2 RELAY PICKUP ALARM | PICKUP | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 271 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 140 | 0 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2RST | CKT#2 RESET TARGETS | IED | EB1 | 0 | RESET | 0 |  | 1,2,3,4,5,6,7,8 | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | 16 | 47 | 38 | 12 | 1 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2SLO | CKT#2 SLOW OPERATION ALM | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 280 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2SPR | CKT#2 SPRING CHARGE ALRM | IED | EB1 | 0 | CHRGED | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 276 | 1 | 0 | 1 | 10 | 28 | CHRGED | DISCHG |  |  | CHRGED | DISCHG | 140 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2TCM | CKT#2 TRIP COIL FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 270 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2TGA | CKT#2 A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 267 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2TGB | CKT#2 B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 268 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2TGC | CKT#2 C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 269 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2TGN | CKT#2 NEUTRAL TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 285 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F2TIM | CKT#2 TIME TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 286 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3-A | CKT #3 A-PHASE CURRENT | CURRENT | EB1 | 0 |  | 181 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 573 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F3-B | CKT #3 B-PHASE CURRENT | CURRENT | EB1 | 0 |  | 227 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 574 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F3-C | CKT #3 C-PHASE CURRENT | CURRENT | EB1 | 0 |  | 116 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 575 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F3-N | CKT #3 NEUTRAL CURRENT | CURRENT | EB1 | 0 |  | 102 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 576 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F369EM | CKT#3 MECHANICAL TRIP | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 311 | 1 | 0 | 1 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3ALT1 | CKT#3 ALT MIN TRIP | IED | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 289 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 78 | 12 | 1 | 1 | 16 | 47 | 78 | 12 | 1 | 1 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3AR | CKT#3 AUTO-RECLOSE | AUTORCL | EB1 | 0 | AUTO | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 291 | 1 | 0 | 0 | 0 | 3 | 1-SHOT | AUTO |  |  | 1-SHOT | AUTO | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 79 | 12 | 1 | 4 | 16 | 47 | 79 | 12 | 1 | 3 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3BKR | CKT#3 EBYP | FDR BKR | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 290 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 140 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 16 | 47 | 150 | 12 | 1 | 41 | 16 | 47 | 151 | 12 | 1 | 21 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3CAP | FEEDER #3 CAP IN SERVICE | KVAR | EB1 | 0 |  | 600 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,F3COM | CKT#3 COMM. FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 288 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3ENB | CKT#3 CONTROL FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 293 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3GT | CKT#3 GROUND TRIP | GNDTRIP | EB1 | 0 | NORMAL | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 292 | 1 | 0 | 0 | 0 | 4 | BYPASS | NORMAL |  |  | BYPASS | NORMAL | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 75 | 12 | 1 | 0 | 16 | 47 | 75 | 12 | 1 | 1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3HLT | CKT#3 HOT LINE TAGGED | AUTORCL | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 317 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 20 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3INS | CKT#3 INST TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 320 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3INSB | CKT#3 INST TRIP BLOCK | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 308 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3KVAR | CKT#3 KVAR DEMAND | KW | EB1 | 0 |  | 357 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 581 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F3KW | CKT#3 KW DEMAND | KW | EB1 | 0 |  | 3720 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 580 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KW | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F3LOAC | CKT#3 LOSS OF AC ALARM | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 310 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3LODC | CKT#3 LOSS DC ALARM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 306 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3LOUT | EBYP FDR LOCKOUT #3 | FDR LO | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 305 | 1 | 0 | 0 | 0 | 12 | RESET | LCKOUT |  |  |  |  | 141 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3LR | CKT#3 LOCAL/REMOTE | IED | EB1 | 0 | REMOTE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 312 | 1 | 0 | 1 | 0 | 21 | LOCAL | REMOTE |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3PF | FEEDER #3 PF CALC | PFACTOR | EB1 | 0 |  | 0.99525 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F3PF-T | CKT#3 PF TELEMETERED | PFACTOR | EB1 | 0 |  | -2.27 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 582 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | -0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F3PUA | CKT#3 RELAY PICKUP ALARM | PICKUP | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 304 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 140 | 0 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3RST | CKT#3 RESET TARGETS | IED | EB1 | 0 | RESET | 0 |  | 1,2,3,4,5,6,7,8 | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | 16 | 47 | 60 | 12 | 1 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3SLO | CKT#3 SLOW OPERATION ALM | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 313 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3SPR | CKT#3 SPRING CHARGE ALRM | IED | EB1 | 0 | CHRGED | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 309 | 1 | 0 | 1 | 10 | 28 | CHRGED | DISCHG |  |  | CHRGED | DISCHG | 140 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3TCM | CKT#3 TRIP COIL FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 303 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3TGA | CKT#3 A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 300 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3TGB | CKT#3 B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 301 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3TGC | CKT#3 C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 302 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3TGN | CKT#3 NEUTRAL TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 318 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F3TIM | CKT#3 TIME TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 319 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4-A | CKT #4 A-PHASE CURRENT | CURRENT | EB1 | 0 |  | 101 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 590 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F4-B | CKT #4 B-PHASE CURRENT | CURRENT | EB1 | 0 |  | 89 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 591 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F4-C | CKT #2 C-PHASE CURRENT | CURRENT | EB1 | 0 |  | 125 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 592 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F4-N | CKT #4 NEUTRAL CURRENT | CURRENT | EB1 | 0 |  | 36 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 593 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F469EM | CKT#4 MECHANICAL TRIP | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 344 | 1 | 0 | 1 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4ALT1 | CKT#4 ALT MIN TRIP | IED | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 322 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 100 | 12 | 1 | 1 | 16 | 47 | 100 | 12 | 1 | 1 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4AR | CKT#4 AUTO-RECLOSE | AUTORCL | EB1 | 0 | AUTO | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 324 | 1 | 0 | 0 | 0 | 3 | 1-SHOT | AUTO |  |  | 1-SHOT | AUTO | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 101 | 12 | 1 | 4 | 16 | 47 | 101 | 12 | 1 | 3 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4BKR | CKT#4 EBYP | FDR BKR | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 323 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 140 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 16 | 47 | 152 | 12 | 1 | 41 | 16 | 47 | 153 | 12 | 1 | 21 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4CAP | FEEDER #4 CAP IN SERVICE | KVAR | EB1 | 0 |  | 1200 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,F4COM | CKT#4 COMM. FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 321 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4ENB | CKT#4 CONTROL FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 326 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4GT | CKT#4 GROUND TRIP | GNDTRIP | EB1 | 0 | NORMAL | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 325 | 1 | 0 | 0 | 0 | 4 | BYPASS | NORMAL |  |  | BYPASS | NORMAL | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 97 | 12 | 1 | 0 | 16 | 47 | 97 | 12 | 1 | 1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4HLT | CKT#4 HOT LINE TAGGED | AUTORCL | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 350 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 20 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4INS | CKT#4 INST TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 353 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4INSB | CKT#4 INST TRIP BLOCK | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 341 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4KVAR | CKT#4 KVAR DEMAND | KW | EB1 | 0 |  | -732 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 598 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F4KW | CKT#4 KW DEMAND | KW | EB1 | 0 |  | 2176 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 597 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KW | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F4LOAC | CKT#4 LOSS OF AC ALARM | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 343 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4LODC | CKT#4 LOSS DC ALARM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 339 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4LOUT | EBYP FDR LOCKOUT #4 | FDR LO | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 338 | 1 | 0 | 0 | 0 | 12 | RESET | LCKOUT |  |  |  |  | 141 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4LR | CKT#4 LOCAL/REMOTE | IED | EB1 | 0 | REMOTE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 345 | 1 | 0 | 1 | 0 | 21 | LOCAL | REMOTE |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4PF | FEEDER #4 PF CALC | PFACTOR | EB1 | 0 |  | -0.94781 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F4PF-T | CKT#4 PF TELEMETERED | PFACTOR | EB1 | 0 |  | -0.94 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 599 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | -0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F4PUA | CKT#4 RELAY PICKUP ALARM | PICKUP | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 337 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 140 | 0 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4RST | CKT#4 RESET TARGETS | IED | EB1 | 0 | RESET | 0 |  | 1,2,3,4,5,6,7,8 | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | 16 | 47 | 82 | 12 | 1 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4SLO | CKT#4 SLOW OPERATION ALM | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 346 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4SPR | CKT#4 SPRING CHARGE ALRM | IED | EB1 | 0 | CHRGED | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 342 | 1 | 0 | 1 | 10 | 28 | CHRGED | DISCHG |  |  | CHRGED | DISCHG | 140 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4TCM | CKT#4 TRIP COIL FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 336 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4TGA | CKT#4 A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 333 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4TGB | CKT#4 B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 334 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4TGC | CKT#4 C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 335 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4TGN | CKT#4 NEUTRAL TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 351 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F4TIM | CKT#4 TIME TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 352 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5-A | CKT #5 A-PHASE CURRENT | CURRENT | EB1 | 0 |  | 77 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 607 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 500 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 575 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 650 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F5-B | CKT #5 B-PHASE CURRENT | CURRENT | EB1 | 0 |  | 60 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 608 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 500 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 575 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 650 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F5-C | CKT #5 C-PHASE CURRENT | CURRENT | EB1 | 0 |  | 62 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 609 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 500 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 575 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 650 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F5-N | CKT #5 NEUTRAL CURRENT | CURRENT | EB1 | 0 |  | 19 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 610 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 425 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 475 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 510 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F569EM | CKT#5 MECHANICAL TRIP | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 377 | 1 | 0 | 1 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5ALT1 | CKT#5 ALT MIN TRIP | IED | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 355 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 122 | 12 | 1 | 1 | 16 | 47 | 122 | 12 | 1 | 1 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5AR | CKT#5 AUTO-RECLOSE | AUTORCL | EB1 | 0 | AUTO | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 357 | 1 | 0 | 0 | 0 | 3 | 1-SHOT | AUTO |  |  | 1-SHOT | AUTO | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 123 | 12 | 1 | 4 | 16 | 47 | 123 | 12 | 1 | 3 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5BKR | CKT#5 EBYP | FDR BKR | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 356 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 140 | 4 | 0 | 0 | 0 | 1 | 0 | 0 | 0 | 16 | 47 | 154 | 12 | 1 | 41 | 16 | 47 | 155 | 12 | 1 | 21 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5CAP | FEEDER #5 CAP IN SERVICE | KVAR | EB1 | 0 |  | 450 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,F5COM | CKT#5 COMM. FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 354 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5ENB | CKT#5 CONTROL FAILURE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 359 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5GT | CKT#5 GROUND TRIP | GNDTRIP | EB1 | 0 | NORMAL | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 358 | 1 | 0 | 0 | 0 | 4 | BYPASS | NORMAL |  |  | BYPASS | NORMAL | 11 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 119 | 12 | 1 | 0 | 16 | 47 | 119 | 12 | 1 | 1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5HLT | CKT#5 HOT LINE TAGGED | AUTORCL | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 383 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 20 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5INS | CKT#5 INST TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 386 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5INSB | CKT#5 INST TRIP BLOCK | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 374 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5KVAR | CKT#5 KVAR DEMAND | KW | EB1 | 0 |  | 201 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 615 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F5KW | CKT#5 KW DEMAND | KW | EB1 | 0 |  | 1410 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 614 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KW | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F5LOAC | CKT#5 LOSS OF AC ALARM | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 376 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5LODC | CKT#5 LOSS DC ALARM | IED | EB1 | 0 | RESET | 0 |  | 1,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 372 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 129 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5LOUT | EBYP FDR LOCKOUT #5 | FDR LO | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 371 | 1 | 0 | 0 | 0 | 12 | RESET | LCKOUT |  |  |  |  | 141 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5LR | CKT#5 LOCAL/REMOTE | IED | EB1 | 0 | REMOTE | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 378 | 1 | 0 | 1 | 0 | 21 | LOCAL | REMOTE |  |  |  |  | 0 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5PF | FEEDER #5 PF CALC | PFACTOR | EB1 | 0 |  | 0.95077 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F5PF-T | CKT#5 PF TELEMETERED | PFACTOR | EB1 | 0 |  | -2.27 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 616 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | % | -0.01 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,F5PUA | CKT#5 RELAY PICKUP ALARM | PICKUP | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 370 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 140 | 0 | 3 | 0 | 0 | 0 | 7 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5RST | CKT#5 RESET TARGETS | IED | EB1 | 0 | RESET | 0 |  | 1,2,3,4,5,6,7,8 | - | MO | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | 16 | 47 | 104 | 12 | 1 | 1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5SLO | CKT#5 SLOW OPERATION ALM | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 379 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5SPR | CKT#5 SPRING CHARGE ALRM | IED | EB1 | 0 | CHRGED | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 375 | 1 | 0 | 1 | 10 | 28 | CHRGED | DISCHG |  |  | CHRGED | DISCHG | 140 | 0 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5TCM | CKT#5 TRIP COIL FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 369 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5TGA | CKT#5 A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 366 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5TGB | CKT#5 B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 367 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5TGC | CKT#5 C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 368 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5TGN | CKT#5 NEUTRAL TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 384 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,F5TIM | CKT#5 TIME TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 385 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,L1ATMN | LTC#1 AUTO/MAN | VOLTREG | EB1 | 0 | AUTO | 0 |  | 1,2,3,4,5,6,7,8 | - | MO | 16 | 47 | 211 | 1 | 0 | 0 | 0 | 38 | AUTO | MANUAL |  |  | AUTO | MANUAL | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,L1COM | LTC#1 COMMUNICATION ALM | VOLTREG | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 205 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,L1LWR | LTC#1 LOWER COMMAND | VOLTREG | EB1 | 0 | OFF | 0 |  | 1,2,3,4,5,6,7,8 | - | NA | 16 | 47 | 207 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,L1NEUT | LTC#1 NEUTRAL TAP POS. | VOLTREG | EB1 | 0 | OFF | 0 |  | 1,2,3,4,5,6,7,8 | - | NA | 16 | 47 | 208 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,L1RAS | LTC#1 RAISE COMMAND | VOLTREG | EB1 | 0 | OFF | 0 |  | 1,2,3,4,5,6,7,8 | - | NA | 16 | 47 | 206 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,L1REVP | LTC#1 T1 POWER FLOW REV. | VOLTRED | EB1 | 0 | UP | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 209 | 1 | 0 | 0 | 0 | 1 | UP | DOWN |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 3 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,LOCAL | ALL EBYP FBKRS IN LOCAL | IED | EB1 | 0 | REMOTE | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 223 | 1 | 0 | 0 | 0 | 21 | LOCAL | REMOTE |  |  |  |  | 2 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,M1-A | BUS #1 A-PHASE CURRENT | CURRENT | EB1 | 0 |  | 513.59 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 626 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 0.097659 | 0 | 0 | 1000 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 1200 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 1390 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1-B | BUS #1 B-PHASE CURRENT | CURRENT | EB1 | 0 |  | 513.785 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 627 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 0.097659 | 0 | 0 | 1000 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 1200 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 1390 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1-C | BUS #1 C-PHASE CURRENT | CURRENT | EB1 | 0 |  | 462.905 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 628 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 0.097659 | 0 | 0 | 1000 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 1200 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 1390 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1-N | BUS #1 N-PHASE CURRENT | CURRENT | EB1 | 0 |  | 0 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 629 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 0.097 | 0 | 0 | 1000 | -1.7e+38 | 15 | 2 | 0 | 0 | 0 | 1200 | -1.7e+38 | 15 | 3 | 0 | 0 | 0 | 1390 | -1.7e+38 | 15 | 4 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1816 | MOAB SWITCH #1816 | MOAB | EB1 | 0 | OPEN | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 219 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,M1817 | MOAB SWITCH #1817 | MOAB | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 218 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,M1818 | MOAB SWITCH #1818 | MOAB | EB1 | 0 | CLOSE | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 216 | 1 | 0 | 1 | 0 | 2 | OPEN | CLOSE |  |  | OPEN | CLOSE | 10 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,M1AMNV | B1 BITRONICS A MIN VOLT | VOLTAGE | EB1 | 0 |  | 25958 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 684 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1AMX1 | B1 BITRONICS A MAX AMPS | CURRENT | EB1 | 0 |  | 8238 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 680 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1AMXV | B1 BITRONICS A MAX VOLT | VOLTAGE | EB1 | 0 |  | 27329 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 688 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1BMNV | B1 BITRONICS B MIN VOLT | VOLTAGE | EB1 | 0 |  | 25726 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 685 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1BMX1 | B1 BITRONICS B MAX AMPS | CURRENT | EB1 | 0 |  | 8267 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 681 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1BMXV | B1 BITRONICS B MAX VOLT | VOLTAGE | EB1 | 0 |  | 27206 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 689 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1CMNV | B1 BITRONICS C MIN VOLT | VOLTAGE | EB1 | 0 |  | 25673 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 686 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1CMX1 | B1 BITRONICS C MAX AMPS | CURRENT | EB1 | 0 |  | 6823 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 682 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1CMXV | B1 BITRONICS C MAX VOLT | VOLTAGE | EB1 | 0 |  | 27154 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 690 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1COM | SWB#1 M871 COMM. FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 212 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,M1KVAR | BUS #1 REACTIVE POWER | KVAR | EB1 | 0 |  | -660.099 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 652 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KVAR | 2.651 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1KW | BUS #1 KW INST. | KW | EB1 | 0 |  | 10617.3 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 648 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | KW | 2.651 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1MEM | BUS 1 MTR MEMORY LOW | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 217 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,M1NMNV | B1 BITRONICS N MIN VOLT | VOLTAGE | EB1 | 0 |  | 3641 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 687 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1NMX1 | B1 BITRONICS N MAX AMPS | CURRENT | EB1 | 0 |  | 0 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 683 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1NMXV | B1 BITRONICS N MAX VOLT | VOLTAGE | EB1 | 0 |  | 0 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 691 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1PF-T | BUS #1 POWER FACTOR | PFACTOR | EB1 | 0 |  | 0 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 420 | 30 | 0 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | -0.001 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1REC | BUS 1 MTR WAVEFORM TRIG. | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 215 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,M1TEMP | SWB1 BITRONICS TEMP | TEMP | EB1 | 0 |  | 82.4 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 679 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEG F | 0.018 | 32 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1VLTA | BUS #1 VOLTAGE A PHASE | VOLTAGE | EB1 | 0 |  | 118.908 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 631 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 0.0045778 | 0 | 0 | 126.7 | 118.5 | 0.5 | 4 | 4 | 0 | 0 | 128 | 117 | 0.5 | 0 | 0 | 0 | 0 | 129.5 | 115 | 0.5 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1VLTB | BUS #1 VOLTAGE B PHASE | VOLTAGE | EB1 | 0 |  | 118.056 | L | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 632 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 0.0045778 | 0 | 0 | 126.7 | 119 | 0.5 | 4 | 4 | 0 | 0 | 128 | 117 | 0.5 | 0 | 0 | 0 | 0 | 129.5 | 115 | 0.5 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,M1VLTC | BUS #1 VOLTAGE C PHASE | VOLTAGE | EB1 | 0 |  | 117.699 | L | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 633 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | VOLTS | 0.0045778 | 0 | 0 | 126.7 | 118.5 | 0.5 | 4 | 4 | 0 | 0 | 128 | 117 | 0.5 | 0 | 0 | 0 | 0 | 129.5 | 115 | 0.5 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,MAXVR | LTC#1 T1 MAX VOLT RE. | VOLTRED | EB1 | 0 | ON | 0 |  | _,_,3,_,_,_,_,_ | - | MO | 16 | 47 | 210 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 51 | 1 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 16 | 47 | 159 | 12 | 1 | 3 | 16 | 47 | 159 | 12 | 1 | 4 | 0 | 30 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,PCOMM | PERCENT COMMUNICATION | SPARE | EB1 | 0 |  | 100 | N | _,2,3,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,PH1AMX | CKT #1A MAX CURRENT | CURRENT | EB1 | 0 |  | 66 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH1BMX | CKT #1B MAX CURRENT | CURRENT | EB1 | 0 |  | 65 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH1CMX | CKT #1C MAX CURRENT | CURRENT | EB1 | 0 |  | 111 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH2AMX | CKT #2A MAX CURRENT | CURRENT | EB1 | 0 |  | 109 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH2BMX | CKT #2B MAX CURRENT | CURRENT | EB1 | 0 |  | 109 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH2CMX | CKT #2C MAX CURRENT | CURRENT | EB1 | 0 |  | 74 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH3AMX | CKT #3A MAX CURRENT | CURRENT | EB1 | 0 |  | 270 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH3BMX | CKT #3B MAX CURRENT | CURRENT | EB1 | 0 |  | 321 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH3CMX | CKT #3C MAX CURRENT | CURRENT | EB1 | 0 |  | 191 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH4AMX | CKT #4A MAX CURRENT | CURRENT | EB1 | 0 |  | 113 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH4BMX | CKT #4B MAX CURRENT | CURRENT | EB1 | 0 |  | 96 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH4CMX | CKT #4C MAX CURRENT | CURRENT | EB1 | 0 |  | 135 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH5AMX | CKT #5A MAX CURRENT | CURRENT | EB1 | 0 |  | 114 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH5BMX | CKT #5B MAX CURRENT | CURRENT | EB1 | 0 |  | 89 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,PH5CMX | CKT #5C MAX CURRENT | CURRENT | EB1 | 0 |  | 81 | N | _,2,_,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 100
EB1,POLERR | POLE ERROR COUNT | SPARE | EB1 | 0 |  | 16128 | N | _,2,3,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,RTU | EBYP SUB DNP RTU | RTU | EB1 | 0 | OK | 0 |  | 1,2,3,4,5,6,7,8 | - | RT | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 160 | 0 | 4 | 0 | 0 | 0 | 20 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1BCOM | T1 BACKUP RLY COMM FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 38 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1BENB | T1 BACKUP RELAY ENABLE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 39 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1BINS | T1 B INS TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 40 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1BTGA | T1 BACKUP A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 41 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1BTGB | T1 BACKUP B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 42 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1BTGC | T1 BACKUP C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 43 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1BTGN | T1 BACKUP N-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 44 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DCOM | T1 DIFF RLY COMM FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 26 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DDIF | T1 DIFFERENTIAL TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 28 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DENB | T1 DIFF RLY ENABLE | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 27 | 1 | 0 | 0 | 0 | 39 | ALARM | OK |  |  |  |  | 133 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DINS | T1 INST TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 29 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DTGA | T1 A-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 31 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DTGB | T1 B-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 32 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DTGC | T1 C-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 33 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DTGN | T1 N-PH TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 34 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1DTIM | T1 TIME TARGET | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 30 | 1 | 0 | 0 | 0 | 22 | RESET | TRIP |  |  | RESET |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PCOM | T1-PULEO COMM FAIL ALM | ANNUCTR | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 0 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 0 | 1 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PHGA | T1-PULEO HIGH PRESS. ALM | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 2 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PLAC | T1-PULEO LOSS OF AC ALM | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 4 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PLGA | T1-PULEO LOW GAS ALARM | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 3 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PLLL | T1-PULEO LTC1 LOW LMT AL | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 10 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PLNC | T1-PULEO LOW N2 CYL ALM | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 1 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PLOA | T1-PULEO LTC1 LOW OIL AL | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 11 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PLOL | T1-PULEO LOW OIL ALARM | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 7 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PLRL | T1-PULEO LTC1 RAISE LMT | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 9 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1PPRA | T1-PULEO PRESS RELIEF AL | ANNUCTR | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 6 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1QCOM | T1-QUALITROL COM FAIL | IED | EB1 | 0 | OK | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 387 | 1 | 0 | 0 | 0 | 0 | OK | FAIL |  |  |  |  | 133 | 1 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1QDIF | XFMR#1 LTC DIFF TEMP | TEMP | EB1 | 0 |  | 13 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 742 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEG C | 1 | 0 | 0 | 75 | -1.7e+38 | 0 | 4 | 0 | 0 | 0 | 80 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,T1QFAN | T1-QUALITROL FAN RUN S1 | IED | EB1 | 0 | OFF | 0 |  | _,_,3,_,_,_,_,_ | - | NA | 16 | 47 | 409 | 1 | 0 | 0 | 0 | 5 | OFF | ON |  |  | OFF | ON | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1QFF | T1-QUALITROL FAN FAIL S1 | IED | EB1 | 0 | RESET | 0 |  | _,_,3,_,_,_,_,_ | - | SU | 16 | 47 | 408 | 1 | 0 | 0 | 0 | 8 | RESET | ALARM |  |  | RESET |  | 133 | 0 | 4 | 0 | 0 | 0 | 0 | 0 | 0 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | -1 | 0 | 10 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
EB1,T1QFL1 | XFMR #1 FAN BANK1 LOAD | TEMP | EB1 | 0 |  | 0 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 752 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | AMPS | 1 | 0 | 0 | 20 | -1.7e+38 | 0 | 4 | 0 | 0 | 0 | 25 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 50 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,T1QOIL | XFMR #1 OIL TEMP | TEMP | EB1 | 0 |  | 29 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 732 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEG C | 1 | 0 | 0 | 75 | -1.7e+38 | 0 | 4 | 0 | 0 | 0 | 80 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,T1QWND | XFMR #1 WINDING TEMP | TEMP | EB1 | 0 |  | 30 | N | _,2,_,_,_,_,_,_ | - | AL | 16 | 47 | 737 | 30 | 0 | 0 | 30 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | DEG C | 1 | 0 | 0 | 75 | -1.7e+38 | 0 | 4 | 0 | 0 | 0 | 80 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0
EB1,TIMOUT | COMM TIMEOUT ERROR COUNT | SPARE | EB1 | 0 |  | 1112 | N | _,2,3,_,_,_,_,_ | - | AL | -1 | -1 | -1 | -1 | -1 | 0 | 0 | 0 | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | 1.7e+38 | -1.7e+38 | 0 | 0 | 0 | 0 | 0 | -1 | 0 | 0 | 0